## CI NSPS
Engine Category | Date Constructed/ Reconstructed/Manufactured | Emission Standardsa,b,d,e | Fuel Requirementsc,f,e | Importing/Installing Requirements | Monitoring Requirements | Compliance Requirements | Testing Requirements | Notification, Reports, and Records Requirementsg | General Provisions (40 CFR part 60)
Pre-2007 model year non-emergency CI ICE <10 l/cyl | Commenced construction after 7/11/2005 and manufactured after April 1, 2006 | 60.4204(a) Table 1 | 60.4207(a), (b), (e) | 60.4208(a) through (f), (i) | If equipped with diesel particulate filter: 60.4209(b) | 60.4206 60.4211(a), (b), (g) | 60.4212 60.4204(d) | If >2,237 KW (3,000 HP) or >130 KW (175 HP) and not certified: 60.4214(a) If equipped with DPF: 60.4214(c) | Table 8
Pre-2007 model year non-emergency CI ICE 10 l/cyl≤displacement<30 l/cyl | Commenced construction after 7/11/2005 and manufactured after April 1, 2006 | 60.4204(a) 40 CFR 94.8(a)(1) | 60.4207(a), (b), (e) | 60.4208(a)-(i) | If equipped with diesel particulate filter: 60.4209(b) | 60.4206 60.4211(a), (b), (g) | 60.4212 60.4204(d) | 60.4214(a) If equipped with DPF: 60.4214(c) | Table 8
2007 model year and later non-emergency CI ICE <30 l/cyl | Commenced construction after 7/11/2005 and manufactured after April 1, 2006 | 60.4204(b) 60.4201 | 60.4207(a), (b), (e) | 60.4208(a)-(i) | If equipped with diesel particulate filter: 60.4209(b) | 60.4206 60.4211(a), (c), (g) | 60.4212 60.4204(d) | If >2,237 KW (3,000 HP) or >10 l/cyl: 60.4214(a) If equipped with DPF: 60.4214(c) | Table 8
Non-emergency CI ICE ≥30 l/cyl | Commenced construction after 7/11/2005 and manufactured after April 1, 2006 | 60.4204(c)(1) through (4) | 60.4207(a), (d), (e) | 60.4208(a)-(f), (h), (i) | If equipped with diesel particulate filter: 60.4209(b) | 60.4206 60.4211(a), (d), (g) | 60.4213 | 60.4214(a) If equipped with DPF: 60.4214(c) | Table 8
Pre-2007 model year emergency CI ICE <10 l/cyl (except fire pump engines) | Commenced construction after 7/11/2005 and manufactured after April 1, 2006 | 60.4205(a) Table 1 | 60.4207(a), (b), (e) | 60.4208(a), (b), (h), (i) | 60.4209(a) If equipped with diesel particulate filter: 60.4209(b) | 60.4206 60.4211(a), (b), (f), (g) | 60.4212 | 60.4214(b) If equipped with DPF: 60.4214(c) >100 HP and >15 hrs/yr for emergency DR: 60.4214(d) | Table 8
Pre-2007 model year emergency CI ICE 10 l/cyl≤displacement<30 l/cyl (except fire pump engines) | Commenced construction after 7/11/2005 and manufactured after April 1, 2006 | 60.4205(a) 40 CFR 94.8(a)(1) | 60.4207(a), (b), (e) | 60.4208(a), (b), (h), (i) | 60.4209(a) If equipped with diesel particulate filter: 60.4209(b) | 60.4206 60.4211(a), (b), (f), (g) | 60.4212 | 60.4214(b) If equipped with DPF: 60.4214(c) >100 HP and >15 hrs/yr for emergency DR: 60.4214(d) | Table 8
2007 model year and later emergency CI ICE <30 l/cyl (except fire pump engines) | Commenced construction after 7/11/2005 and manufactured after April 1, 2006 | 60.4205(b) 60.4202 | 60.4207(a), (b), (e) | 60.4208(a), (b), (h), (i) | 60.4209(a) If equipped with diesel particulate filter: 60.4209(b) | 60.4206 60.4211(a), (c), (f), (g) | 60.4212 | 60.4214(b) If equipped with DPF: 60.4214(c) >100 HP and >15 hrs/yr for emergency DR: 60.4214(d) | Table 8
Fire pump engines <30 l/cyl manufactured prior to the model years in Table 3 of 40 CFR part 60, subpart IIII | Commenced construction after 7/11/2005 and manufactured as a certified NFPA fire pump engine after July 1, 2006 | 60.4205(c) Table 4 | 60.4207(a), (b), (e) | 60.4208(h), (i) | 60.4209(a) If equipped with diesel particulate filter: 60.4209(b) | 60.4206 60.4211(a), (b), (f), (g) | 60.4212 | 60.4214(b) If equipped with DPF: 60.4214(c) >100 HP and >15 hrs/yr for emergency DR: 60.4214(d) | Table 8
Fire pump engines <30 l/cyl manufactured during or after the model year that applies to your fire pump engine power rating in Table 3 of 40 CFR part 60, subpart IIII | Commenced construction after 7/11/2005 and manufactured as a certified NFPA fire pump engine after July 1, 2006 | 60.4205(c) Table 4 | 60.4207(a), (b), (e) | 60.4208(h), (i) | 60.4209(a) If equipped with diesel particulate filter: 60.4209(b) | 60.4206 60.4211(a), (c), (f), (g) | 60.4212 | 60.4214(b) If equipped with DPF: 60.4214(c) >100 HP and >15 hrs/yr for emergency DR: 60.4214(d) | Table 8
Emergency CI ICE ≥30 l/cyl (except fire pump engines) | Commenced construction after 7/11/2005 and manufactured after April 1, 2006 | 60.4205(d)(1) and (2) | 60.4207(a), (d), (e) | 60.4208(a), (b), (h), (i) | 60.4209(a) If equipped with diesel particulate filter: 60.4209(b) | 60.4206 60.4211(a), (d), (f), (g) | 60.4213 | 60.4214(b) If equipped with DPF: 60.4214(c) >100 HP and >15 hrs/yr for emergency DR: 60.4214(d) | Table 8
Modified/Reconstructed non-emergency CI ICE <30 l/cyl | Modified or reconstructed after 7/11/2005 | Pre-2007 Model Year: 60.4204(a) 2007 Model Year and Later: 60.4204(b) | 60.4207(a), (b), (e) | 60.4208(i) | If equipped with diesel particulate filter: 60.4209(b) | 60.4206 60.4211(a), (e), (g) | 60.4212 60.4204(d) | If >2,237 KW (3,000 HP) or >10 l/cyl or pre-2007 model year and >130 KW (175 HP) and not certified: 60.4214(a) If equipped with DPF: 60.4214(c) | Table 8
Modified/Reconstructed emergency CI ICE <30 l/cyl | Modified or reconstructed after 7/11/2005 | Pre-2007 Model Year: 60.4205(a) 2007 Model Year and Later: 60.4205(b) | 60.4207(a), (b), (e) | 60.4208(i) | 60.4209(a) If equipped with diesel particulate filter: 60.4209(b) | 60.4206 60.4211(a), (e), (f), (g) | 60.4212 60.4204(e) | 60.4214(b) If equipped with DPF: 60.4214(c) >100 HP and >15 hrs/yr for emergency DR: 60.4214(d) | Table 8
Modified/Reconstructed non-emergency CI ICE ≥30 l/cyl | Modified or reconstructed after 7/11/2005 | 60.4204(c)(1) through (4) | 60.4207(a), (d), (e) | 60.4208(i) | If equipped with diesel particulate filter: 60.4209(b) | 60.4206 60.4211(a), (e), (g) | 60.4213 | 60.4214(a) If equipped with DPF: 60.4214(c) | Table 8
Modified/Reconstructed emergency CI ICE ≥30 l/cyl | Modified or reconstructed after 7/11/2005 | 60.4205(d)(1) through (3) | 60.4207(a), (d), (e) | 60.4208(i) | 60.4209(a) If equipped with diesel particulate filter: 60.4209(b) | 60.4206 60.4211(a), (e), (f), (g) | 60.4213 | 60.4214(b) If equipped with DPF: 60.4214(c) >100 HP and >15 hrs/yr for emergency DR: 60.4214(d) | Table 8
NOTE: For the purposes of this subpart, the date that construction commences is the date the engine is ordered by the owner or operator.
aPer 60.4200(e) Owners and operators of facilities with CI ICE that are acting as temporary replacement units and that are located at a stationary source for less than 1 year and that have been properly certified as meeting the standards that would be applicable to such engine under the appropriate nonroad engine provisions, are not required to meet any other provisions under this subpart with regard to such engines.
bPer 60.4215(a) Stationary CI ICE with a displacement of less than 30 liters per cylinder that are used in Guam, American Samoa, or the Commonwealth of the Northern Mariana Islands are required to meet the applicable emission standards in §§60.4202 and 60.4205.
cPer 60.4215(b) stationary CI ICE that are used in Guam, American Samoa, or the Commonwealth of the Northern Mariana Islands are not required to meet the fuel requirements in 40 CFR 60.4207.
dStationary CI ICE with a displacement of greater than or equal to 30 liters per cylinder that are used in Guam, American Samoa, or the Commonwealth of the Northern Mariana Islands are required to meet the emission standards in 60.4215(c).
eSpecial requirements apply to engines used in Alaska. Please refer to §60.4216 for the specific requirements and provisions that apply to eninges that are located in areas of Alaska not accessible by the FAHS.
fPer 60.4217 Owners and operators of stationary CI ICE that do not use diesel fuel may petition the Administrator for approval of alternative emission standards, if they can demonstrate that they use a fuel that is not the fuel on which the manufacturer of the engine certified the engine and that the engine cannot meet the applicable standards required in §60.4204 or §60.4205 using such fuels and that use of such fuel is appropriate and reasonably necessary, considering cost, energy, technical feasibility, human health and environmental, and other factors, for the operation of the engine.
gPer §60.4214(d) owners/operators of emergency stationary RICE >100 HP that operate or that are contractually obligated to be available to operate for >15 hrs/yr for emergency demand response or for voltage/frequency purposes (§60.4211(f)(2)(ii) or (iii)) are subject to §60.4214(d).
Abbreviations:
CI-Compression Ignition
NFPA-National Fire Protecion Association
DPF-Diesel particulate filter
FAHS-Federal Aid Highway System

## Revisions
Date of Revision | Description of Revision
2011-08-22 | Table of Requirements was revised to reflect amendments made to 40 CFR part 60, subpart IIII on June 28, 2011.
2013-01-30 | Revised to reflect January 2013 amendments adding notification requirements (§60.4214(d)) for certain >100 HP emergency engines participating in emergency demand response operation and for voltage/frequency purposes.