LT1SWTR MONTHLY REPORT TO EPA FOR COMPLIANCE DETERMINATION

MEMBRANE FILTRATION SYSTEMS (MF, UL, RO)

(Due to EPA by 10th day of the following month)

Month __________		System/Treatment Plant ______________________________________	PWSID _______________

Year ___________		Type of Filtration ___________________________________________

Combined Effluent Turbidity Performance Criteria (DATA ON PAGE 2)

- Total number of combined effluent filtered water turbidity measurements made = _________

- Total Number of combined effluent filtered water turbidity measurements that are less than or equal to  0.3 NTU = __________

- The percentage of turbidity measurements meeting the specified limits = B/A x 100= ________/________ x 100 = _________%

- Record the date and turbidity value for any measurements exceeding 1 NTU: if none, enter “none”

| Time and Date of Exceedance | Highest Turbidity ( NTU) | Time and Date EPA Was Notified |
| --- | --- | --- |

Disinfection Performance Criteria

Point-of-Entry Minimum Disinfectant Residual Criteria

The minimum residual concentration must not drop below 0.2 mg/L OR the higher value (>0.2 mg/L) needed each day for adequate inactivation of Giardia and viruses.

| Date | Minimum Disinfectant Residual at Point of Entry to Distribution System (mg/L) | Date | Minimum Disinfectant Residual at Point of Entry to Distribution System (mg/L) | Date | Minimum Disinfectant Residual at Point of Entry to Distribution System (mg/L) |
| --- | --- | --- | --- | --- | --- |
| 1 |  | 11 |  | 21 |  |
| 2 |  | 12 |  | 22 |  |
| 3 |  | 13 |  | 23 |  |
| 4 |  | 14 |  | 24 |  |
| 5 |  | 15 |  | 25 |  |
| 6 |  | 16 |  | 26 |  |
| 7 |  | 17 |  | 27 |  |
| 8 |  | 18 |  | 28 |  |
| 9 |  | 19 |  | 29 |  |
| 10 |  | 20 |  | 30 |  |
|  |  |  |  | 31 |  |

| Days the POE Residual Was < 0.2 mg/L |
| --- |
| Time/Day | Duration of Low Level (indicate the hrs) | Time and Date Reported to EPA |

Distribution System Disinfectant Residual Criteria MEASURED WHEN TAKING TCR (BACT) SAMPLES

A = # of samples this month that disinfectant residual was measured in distribution system = ____________

C = # of samples this month that disinfectant residual was NOT detected when you measured = __________

V = C / A * 100 = ___________ %		For the previous month, V = ________%

_____________________________________________________________________________________________________

Prepared by ______________________________________		Date_________________________

MONTHLY REPORTING SHEET FOR COMBINED FILTER EFFLUENT (CFE) TURBIDITY

MEMBRANE FILTRATION SYSTEMS (MF, UL, RO)

MONTH ______________			SYSTEM NAME _____________________________________________

YEAR ________________			PWS ID# _____________________________________________________

REQUIRED # OF 4-HOUR TURBIDITY READINGS/DAY =   ________  (UNLESS PLANT OFF – INDICATE “PO” IN EACH CELL)

**REPORT MAXIMUM TURBIDITY READING THAT DAY, EVEN IF IT WAS BETWEEN 4 HOUR READINGS

DO NOT REPORT RESULTS COLLECTED DURING BACKWASH, FILTER-TO-WASTE, OR ANY TIME WATER IS NOT BEING PRODUCED FOR CONSUMPTION

| DATE | 1ST (NTU) | 2ND (NTU) | 3RD (NTU) | 4TH (NTU) | 5TH (NTU) | 6TH (NTU) | **DAILY MAX (NTU) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  |
| 21 |  |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  |  |
| 23 |  |  |  |  |  |  |  |
| 24 |  |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  |  |
| 26 |  |  |  |  |  |  |  |
| 27 |  |  |  |  |  |  |  |
| 28 |  |  |  |  |  |  |  |
| 29 |  |  |  |  |  |  |  |
| 30 |  |  |  |  |  |  |  |
| 31 |  |  |  |  |  |  |  |

DATE OF LAST CALIBRATION OF CFE TURBIDIMETER _____________________________

DATA SHEET FOR INDIVIDUAL MEMBRANE UNIT

DAILY DIRECT INTEGRITY (DI) TESTS AND REPAIRS

(FILL OUT ONE PAGE PER UNIT/SKID)

MONTH ______________					PWSID # __________________

YEAR ________________					PWS NAME _______________________

MEMBRANE UNIT # ____________________

| Date | Daily DI Test Successful (Indicate Y/N Within Control Limit?) | Describe Results of Triggered** or Unsuccessful DI Tests and any Corrective Actions Taken (Diagnostic tests, module repairs or replacements). Identify serial # of module ** Two 15-min consecutive filtrate turbidity readings exceeding 0.15 NTU triggers DI test – based on turbidity when water is being produced for consumption |
| --- | --- | --- |
| 1 |  |  |
| 2 |  |  |
| 3 |  |  |
| 4 |  |  |
| 5 |  |  |
| 6 |  |  |
| 7 |  |  |
| 8 |  |  |
| 9 |  |  |
| 10 |  |  |
| 11 |  |  |
| 12 |  |  |
| 13 |  |  |
| 14 |  |  |
| 15 |  |  |
| 16 |  |  |
| 17 |  |  |
| 18 |  |  |
| 19 |  |  |
| 20 |  |  |
| 21 |  |  |
| 22 |  |  |
| 23 |  |  |
| 24 |  |  |
| 25 |  |  |
| 26 |  |  |
| 27 |  |  |
| 28 |  |  |
| 29 |  |  |
| 30 |  |  |
| 31 |  |  |

If Plant Not Operating Indicate “PO”

Date of Last Chemical Cleaning (CIP) of the Membrane Unit _____________________________

Was DI Test Acceptable After Cleaning?  __________________________________

Date of last Calibration of Individual Unit Filtrate Turbidimeter(s) _____________________________